This is an nVent RAYCHEM specification. It is intended to be a supplement to the nVent RAYCHEM: SECTION 220533 HEAT TRACING FOR PLUMBING PIPING SPECIFICATIONS (XL-Trace). A qualified design professional should review and edit the document to suit project requirements.

For more information, contact RAYCHEM, a brand of nVent, 899 Broadway St., Redwood City, CA 94025-1146; Phone: 800-545-6258; Website: www.nvent.com/RAYCHEM

SECTION 220533 HEAT TRACing for plumbing piping 
Services supplement

General

general requirements

The Heat Trace Installer shall provide a complete engineered heat trace system including drawings, details, electrical data and literature required for a complete system, to be supplied by the manufacturer.

The manufacturer shall provide the Layout Drawings in PDF format. 
(Note for Canada: All engineering deliverables to be stamped by a P. Eng. registered in the Province or State. Engineering company must be a valid holder of a Certificate of Authorization in the Province or State.

drawing requirements

Heat Trace Circuit Layout Drawings: Drawings shall be provided, including:

Location/Identification of area to be traced

Heater circuit number

Electrical load

Heater catalog numbers

Heater termination points

Start-up Temperature

Location of all components

Material list of all components and quantities

Heating cable layout

Heat Trace Isometric:

Location of line

Piping line numbers and dimension

Valves, pumps, flanges, fittings, instruments

Heater circuit number

Heat loss and heater output

Electrical load

Heater catalog number

Heater termination points

Design parameters

Insulation type and thickness

Position of all components

Material schedule listing all components and quantities used

Panel ID number

Pipe freeze protection Detail Drawings: Project Specific Installation Detail Drawings shall be provided including details showing:

Installation and positioning of all components

Proper amounts of tracing for valves, pumps, flanges, fittings, instruments, etc.

Junction box layouts

Control Panel Drawings: Drawings shall be provided for each control panel and shall include the following:

Physical arrangement and structural detail drawings.

Complete power and control wiring diagrams showing all internal wiring connections for all electrical and instrument components in each control panel. All wires, terminals, and devices shall be numbered and tagged in accordance with the system elementary diagrams.

System Wiring Diagram: Project Specific drawings including:

Interconnect of all major components

Assignment of circuiting

Connection of circuit wiring in terminal blocks

Connection of sensor wiring

Connection of external alarm wiring (if applicable)

Controller Setpoint Schedule (if applicable) showing the following:

Circuit addresses

Circuit set points

Circuit alarms and settings

Execution

Installation

Installation of the pipe heat trace cable system to be carried out by an experienced heating cable installer. (Tracer Industries Canada Limited).

Contractor shall have a minimum of 10 years of experience in the installation of such systems.

In the field, all heating cables shall be meggered with a minimum of 1000 volts DC for MI cable and 2,500 volts DC for self-regulating cable. The following separate field megger readings shall be taken on each self-regulating and each mineral insulated heating cable:

Heating cable shall be meggered when received at jobsite before installation.

Heating cable shall be meggered after installation, but before concrete is poured.

Heating cable shall be meggered while the concrete is poured.

Heating cable shall be meggered at final commissioning prior to being energized.

All results must meet manufacturer’s specification.

Field Quality Control

Initial start‐up and field testing (commissioning) of the system shall be performed by factory technician or factory representative per the owner’s requirements.

Field Tests And Inspections

The system shall be commissioned in accordance to the manufacturer’s Installation and Operation manual.

Field visits to be scheduled at the following intervals:

Pre-installation training

Heating cable shall be meggered after installation, but before concrete is poured

Heating cable shall be meggered after concrete pour

Final commissioning including controller programming (if applicable)

The technician shall verify that the controller parameters are set to the application requirements.

The technician shall verify that the controller alarm contacts are properly connected to the BMS (if applicable).

System Startup

All commissioning results will be recorded and submitted.

End of Section